Recommended Specifications for

Stravifloor Channel

Section 13 48 00 Sound Control

This document is for specification writers' reference in the drafting process. CDM Stravitec will not be held responsible for the use or unauthorized modification of any information contained herein.

Specification notes are identified in the document as follows “SPEC NOTE” – these notes must be removed from final documents. Where multiple options may be available, these are identified in the corresponding spec note.

Text highlighted in yellow indicates text that should be coordinated with the entire spec book or represent sections that are options not found on every installation.

This document specification has been specifically written for the Stravifloor Mount system. Below is a schematic indication of the construction process from start to end as described in this specification.

- GENERAL

  - Summary

    - Section Includes:

      - The Scope of Work includes for Products and/or Systems to isolate a floating floor from the building structure (Floating Floor Assembly) by means of discrete acoustical isolators under continuous flooring panels and separated from perimeter by acoustical isolation board.

  - Related SECTIONS

    - The work under this section must consider the following sections:

      - Submittal Procedures: Section 01 33 00

      - Quality Control: Section 01 45 00.

      - Close-Out Procedures: Section 01 77 00

      - Subflooring: Section 06 16 23

      - Joint Sealants:  Section 07 92 00

SPEC NOTE:

- Stravifloor Mount systems require a flat and level structural floor to be specified. (Note to Specifier: FF 25 as minimum – meaning a single 6 mm( ¼’’) defect across 3 m (10-feet)).

- Caulking: to be coordinated with appropriate specification or specified herein. Care should be taken to identify the proper acoustical caulking if in separate spec section.

  - Administrative Requirements

    - Coordination:

      - Closely coordinate and carry out jointly this Work with other trades.

      - Place only sufficient insulation modules to permit placing flooring panels without disturbing insulation materials.

      - Do not run heavy equipment over floating floor.

    - Conduct pre-installation readiness site reviews:

      - Manufacturer or its representative shall attend a pe-installation readiness site review meeting to ascertain conditions prior to installation.

    - Conduct post-installation site review:

      - Manufacturer or its representative shall attend a post-installation site review meeting and confirm that installation has been conducted as per its instruction manuals.

      - Identified non-conformities must be rectified prior to installation of additional topping layers.

  - Submittals

    - Submit required submittals in accordance with Section 01 33 00.

    - Product data sheets:

      - Submit manufacturer’s Product data sheets for Products and/or Systems proposed for use in the Scope of Work, including installation requirements, setting drawings, templates, installation requirements, and directions for installation of proposed solutions.

    - Shop Drawings:

      - Submit engineered Shop Drawings.

      - In addition to the requirements of Section 01 33 00, Shop Drawings shall include the following information:

        - Identification of project load conditions – Dead (DL), Live (LL), Superimposed (SiDL) loads.

        - If concentrated loads are imposed on the System, then indicate Concentred Loads and type of load – i.e. point, linear and/or area.

        - Identification of project Acoustic Design Load (ADL) and Serviceability Limit State (SLS) for all different load scenarios.

SPEC NOTE:

Unless stated otherwise the Acoustic Design Load (ADL) and Serviceability Limit State (SLS) shall be calculated as follows:

ADL = DL + 100% SiDL + 25 % LL

and

SLS = DL + 100% SiDL + 100 % LL

      - Shop Drawings shall also include Drawings indicating:

        - Include a floor plan layout with all loads indicated.

        - Include a floor plan layout presenting all penetrations.

        - Include a floor plan layout of all isolators to be installed on-site, including identification of additional isolators needed to support concentrated loads.

        - Include information regarding the size of all isolators on all plans.

        - Include information related to spacing of all isolators.

        - Include information related to the plywood layout, orientation, and installation.

        - [OPTION] Include an Assembly Plan with all “off-site” prefabricated panels numbered and sequence of assembly on-site

SPEC NOTE:

Item above should be removed if Item 2.5 of this spec section is removed.

      - Shop Drawings shall also include Calculations indicating:

        - All design assumptions regarding loading designs, at a minimum ADL and SLS shall be presented for all load areas.

        - Provide design loads (DL and ADL) and Serviceability Limit State (SLS) for all isolators used on the project.

        - Provide deflection and resonance frequency for each isolator indicated in the drawings and for all load conditions.

        - [OPTION] If large horizontal loads are present, provide calculations for Acoustic Lateral Load Bearing Restrain Isolator Pads to restrain Acoustical Isolated Floating Floor.

SPEC NOTE:

Item above should be removed if Item 2.4 .6 of this spec section is removed.

        - Calculations shall be presented in a clear and comprehensive manner so that they can be easily reviewed. Incomplete or haphazard calculations will not be reviewed and lead to Shop Drawing being rejected.

      - Shop Drawings shall also include the following additional information:

        - Dynamic (resonance frequency with load curves) and Static (deflection with load curves) property curves for all isolators used on the plan view.

        - Acoustical test data from an independent laboratory showing required STC and IIC ratings for the floating floor assembly, with tests conducted within the last 10 years.

        - Material datasheet for all other materials used in the design of the Floating Floor Assembly.

SPEC NOTE:

Item above relative to Acoustical test data references a requirement for “tests conducted within the last 10 years”. It should be noted that this is different from the test report as it is common practise for laboratories to re-issue reports with new test report dates for testing that occurred outside of a 10-year test date.

  - Closeout Submittals

    - Submit closeout documentation in accordance with Section 01 77 00.

    - Operation and maintenance data:

      - If applicable, submit Manufacturer’s operation and maintenance instructions for inclusion in the operation and maintenance manuals

- PRODUCTS

  - Acceptable Floor Isolation Systems

    - Stravifloor Mount by CDM Stravitec

SPEC NOTE:

CDM Stravitec, Ltd.

100 Sunrise Avenue, Unit 202, Toronto, Ontario, M4A 1B3

Phone: (905) 265-7401

Email: info-ca@cdm-stravitec.com

Web: www.cdm-stravitec.com

  - Performance/Design Requirements:

    - Intent:

      - Isolated floating floor system shall consist of flooring panels as described in 3.1 .1 and 50 mm (2”) vibration isolators.

      - The air cavity between the isolated floating floor system and base structural floor shall be minimum 50 mm (2”).

SPEC NOTE:

A standard Isolated Floating Floor Isolator is 50 mm (2’’) in height for most system manufacturers. This is the most common air cavity.

However, in order to reduce air stiffness in the cavity a higher cavity may be required per Acoustic Design.

Higher air cavity depths can be achieved by using over-heights (a.k.a. shims).

Additional information on over-heights is provided as a spec note on the Materials part of this section.

      - Isolated floating floor shall be isolated from adjacent structures (e.g. walls, columns and/or curbs) by means of perimeter isolation board material.

      - Floor penetrations such as piping, conduits and drains shall be isolated from the isolated floating floor by use of adequate isolation materials such as the perimeter isolation board material.

      - Floor drains to be used on the isolated floating floor shall consist of two-piece isolated drains.

      - Equipment on top of the isolated floating floor shall be mounted as indicated on drawings and/or acoustical report.

    - Performance Requirements:

      - Isolated floating floor system shall have the following minimum acoustic ratings:

        - STC-62

        - IIC-63

        - Testing to be conducted by an independent laboratory.

        - All testing to be conducted in the last 10-years.

Stravi-dB:

CDM Stravitec provides various acoustic tests for different floor setups on www.stravi-dB.com. In addition to the test reports, editable .csv files with data and typical cross-sections are also available.

      - Vibration isolation material to achieve a minimum 8 Hz resonance frequency at the Acoustic Design Load.

SPEC NOTE:

A standard Isolated Floating Floor Isolator of 50 mm (2’’) in height is capable of achieve 8-10 Hz resonance frequency.

A smaller isolator (less than 50 mm (2’’)) can be provided; for instance, a 30 mm (1-3/16’’) thick isolator would result in a resonance frequency of approximately 10 Hz.

Lower resonance frequencies can be achieved with elastomeric isolators and steel springs. For the Stravifloor Mount the preferred use is with only elastomeric isolators. For a design with lower resonance frequencies, modifications should be done to:

1. Thickness and type of flooring panels (i.e., higher density panel systems to be used as interlayers)

2. Type of isolator (i.e., moving to a steel spring system)

Please contact CDM Stravitec for assistance with the design of special floating floors with low resonance frequency.

For systems using steel springs, a Stravifloor Channel, Deck or Jackup-R is recommended instead.

  - Materials

    - Flooring panels:

      - Plywood: Two layers of 19 mm (3/4”) thick exterior grade Douglas Fir plywood, solid 2 sides to CSA O121-08.

      - [ALTERNATE WORDING]: Flooring panels should be designed to achieve a deflection criterion of L/360 based on dead load, live load and isolator spacing requirements unless noted otherwise.

SPEC NOTE:

Deflection criteria as identified by Engineer of Record.

The appendix of this specification includes sample calculations for the type and quantity of flooring panels (based on engineered wood panels).

The bearing spacing will directly affect the overall performance of the system.

Other materials may be considered for installation as part of the flooring panels – such as wood-cement boards, gypsum boards, gypsum fibre screed boards, MgO based panels and/or high-strength, gypsum-based, reinforced concrete panels. Such applications shall be defined by the acoustical and structural engineer of the record for the project.

    - Support Channels:

      - Minimum 24-gauge galvanized Steel Channels to distribute loads between pads and provide support for Formwork Panels. Channel profile, dimensions and section properties shall be selected based on the loading conditions and isolator spacing and dimensions.

    - Vibration Isolators:

      - Vibration Isolators shall be spaced taking into consideration the loads imposed and formwork type and thickness selected.

      - Vibration Isolators shall be chosen by the manufacturer to ensure that the performance requirements set in this section.

      - The Vibration Isolators shall have a creep rate < 1.5% (dec./min.) at maximum static load.

SPEC NOTE:

In the text above no indication is made to the spacing of isolators. In previous specification sections, standard maximum distances of 600 mm (~24”) are mentioned.

CDM Stravitec does not recommend using this as a base as it may provide erroneous guidance on the distribution of isolators. Isolator spacing, including maximum spacing between isolators, should be defined based on both the loads imposed on the formwork (including loads during construction) and the type and thickness of the formwork used.

    - Perimeter Isolation Board: glass fiber performed boards with a minimum 20 mm (3/4”) thick, with an apparent density of 96 kg/m3 (6 lbs/ft3). [OPTION] Perimeter Isolation Board shall be Formaldehyde-Free.

SPEC NOTE:

CDM Stravitec recommends one of two potential Perimeter Board:

1. Standard Item: Johns Manville Whispertone Wallboard - fine, rotary-process, borosilicate glass fibers bonded with a special thermosetting resin to produce a structurally rigid board-type insulation.

2. Formaldehyde-Free Item: Knauf Acoustical Smooth Board with ECOSE® Technology - inorganic glass fibers preformed into boards with ECOSE Technology. W/ UL Environment: GREENGUARD Certified, GREENGUARD Gold Certified, Validated to be Formaldehyde-Free and EUCEB Certified

Alternatively, use of a 3/8’’ (10 mm) resilient perimeter isolation strip with a minimum density of 20 lbs/cu-ft (320 kg/m3) in areas where seismic loading is considered is recommended.

    - Acoustical Batt Insulation: Mineral wood batt insulation with a minimum 38 mm (1-1/2”) thick, with an apparent density of 40 kg/m3 (2.5 lbs/ft3). [OPTION] Acoustical Batt Insulation shall be Formaldehyde-Free.

SPEC NOTE:

As a reference the thickness of the Acoustical Batt Insulation should be at least 75% of the cavity depth. So, for a 50 mm (2’’) air cavity a 37.5 (1-1/2’’) mm Acoustical Batt Insulation is recommended.

CDM Stravitec recommends one of two potential Acoustical Batt Insulation:

1. Standard Item: Rockwool Acoustical Fire Batt (AFB) - lightweight, acoustical fire batt stone wool insulation specifically designed for steel stud and wood stud interior wall and floor applications – OR EQUIVALENT. This will depend on supply chain at time of project delivery.

2. Formaldehyde-Free Item: Knauf KN Series with ECOSE® Technology - flexible to semi-rigid blankets made from inorganic glass fibers bonded with ECOSE Technology. W/ UL Environment: GREENGUARD Certified, GREENGUARD Gold Certified, Validated to be Formaldehyde-Free and EUCEB Certified

    - Perimeter Sealant Compound: Non-hardening, drying or bleeding, trowel or pour grade sealant.

SPEC NOTE:

CDM Stravitec recommends the use of Tremco Acoustical Sealant or equivalent.

    - [IF REQUIRED] Over-heights: When applicable to create larger air cavities Over-heights (or shims) can be used. Over-heights shall comply with the following conditions:

      - Be made of rigid materials that can withstand the pressures imposed on the Vibration Isolators. Materials like concrete blocks, metal shims or wood shims/sleepers are appropriate. Material choice should take into consideration the potential presence of moisture or water.

      - Be at least 25 mm (1”) larger than the isolator dimensions on all directions.

      - Isolators shall be adhered to the shims.

      - No limits are imposed regarding maximum height, but an interconnection system should be considered to make the overall system stable if it is too high. The interconnected system should secure the Over-height/Vibration Isolation assembly formwork.

- EXECUTION

  - Installation

SPEC NOTE:

Select & keep items #1. to #8. for systems to be assembled on-site

    - Setting of Isolated Floating Floor materials shall be performed by or under supervision of isolation manufacturer and/or its representatives.

    - Install perimeter isolation board around walls, columns, curbs, and vertical penetrations.

    - If concentrated loads are identified on the Shop Drawings identify the location of the loads in advance of placement of vibration isolators.

    - Set gridline for isolators on structural slab.

    - Place individual Isolated channels [OPTION: with designed Over-heights] on top of structural slab in accordance with reviewed and approved Shop Drawings.

    - Place Acoustical Batt Insulation in cavity. Acoustical Batt Insulation shall be installed between channels (neve under the channels)

    - Place flooring panels (i.e. plywood) on top of Isolated Channels and ensure that different panels are set tight against each other and secured with tie-plates. Joints should be staggered in one of the directions of the panels.

    - Perimeter isolation board on walls, columns, curbs, and vertical penetrations shall be also covered with bond breaking material.

  - Field Quality Control

    - Manufacturer shall have established a Quality Control plan in accordance with Section 01 45 00.

    - Manufacturer’s field review to be in accordance with Section 01 45 00.

    - Upon completion, the Manufacturer or its representative is to submit a report attesting to the proper installation of the Acoustically Isolated Floating floor.

  - Protection

    - Ensure that sound isolation is not disturbed or damaged during placing of formwork or concrete.

    - Ensure that waterproofing membrane, if any, is not disturbed or damaged during placing of Sound Isolated Floating floor.

END OF SECTION

APPENDIX -

C.1 Typical thickness and type of panel based on 100 psf (5 kN/m2) LL + 25 psf (1.2 kN/m2) DL, considering 2x:

Deflection criteria L/360:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 7/16" | 7/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 23/32" 3/4" | 23/32" 3/4" | 23/32" 3/4" | 23/32" 3/4" | 23/32" 3/4" | 23/32" 3/4" | 23/32" 3/4" | 19/32" |

Deflection criteria L/240:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" |

Deflection criteria L/180:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 19/32" 5/8" | 19/32" 5/8" | 15/32" 1/2" | 15/32" 1/2" | 19/32" 5/8" | 19/32" 5/8" | 15/32" 1/2" | 19/32" |

C.2 Typical thickness and type of panel based on 60 psf (3 kN/m2) LL + 25 psf (1.2 kN/m2) DL, considering 2x:

Deflection criteria L/360:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" |

Deflection criteria L/240:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 19/32" 5/8" | 19/32" 5/8" | 15/32" 1/2" | 15/32" 1/2" | 19/32" 5/8" | 19/32" 5/8" | 15/32" 1/2" | 19/32" |

Deflection criteria L/180:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 19/32" |

C.3 Typical thickness and type of panel based on 40 psf (2 kN/m2) LL + 25 psf (1.2 kN/m2), considering 2x:

Deflection criteria L/360:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 19/32" 5/8" | 19/32" 5/8" | 15/32" 1/2" | 15/32" 1/2" | 19/32" 5/8" | 19/32" 5/8" | 19/32" 5/8" | 19/32" |

Deflection criteria L/240:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 19/32" |

Deflection criteria L/180:

| Span center-to-center of bearings | Plywood Sheathing | Plywood Structural I Sheathing | Plywood Stud-I-Floor | Plywood Structural Stud-I-Floor | OSB Sheathing | OSB Structural I Sheathing | OSB Stud-I-Floor | Sanded Plywood |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 12'' (305 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 16'' (406 mm) | 5/16" | 5/16" | 15/32" 1/2" | 15/32" 1/2" | 5/16" | 5/16" | 15/32" 1/2" | 19/32" |
| 24'' (610 mm) | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 15/32" 1/2" | 7/16" | 7/16" | 15/32" 1/2" | 19/32" |